| Resilient Seal Gate Valve RSV Gate Valve, Cast Iron Body, EPDM Gate, Non Rising Spindle, Clockwise Closing, Hanwheel and Cap Top, Stainless Steel Spindle, 16 Bar Rated, SABS 664. Sizes 80mm to 300mm... |  |
| --- | --- |

Operating Conditions

| Working Pressure | 16 bars (non shock) |
| --- | --- |
| Working Temperature | Up to 70°C |

Hydrostatic Test Pressure

| Shell Test | 1.5 x PN Rating | 24 bars (non shock) |
| --- | --- | --- |
| Seat Test | PN Rating | 16 bars (non shock) |

Description and Materials Specifications

| Item | Description | Material | Material specification |
| --- | --- | --- | --- |
| 1 | Body | Ductile Iron (Epoxy Coated) | BS 2789 Grade 500-7 |
| 2 | Bonnet | Ductile Iron (Epoxy Coated) | BS 2789 Grade 500-7 |
| 3 | Handwheel | Ductile Iron (Epoxy Coated) | BS 2789 Grade 500-7 |
| Epoxy Coating | For Item 1, 2 & 3 | Electrostatically Applied Epoxy Resin Coated Externally & internally |  |
| 4 | Wedge Gate | Ductile Iron (Fully vulcanized with EPDM Liner | BS 2789 Grade 500-7 |
| 5 | Stem Nut | Bronze / Gunmetal | BS 970 431S29 or 304 S31 |
| 6 | Stem (Spindle) | Stainless Steel | BS 970 431S29 or 304 S31 |
| 7 | Bonnet Bolts | Stainless Steel (Hexagon Socket cap Screw) | 304 |
| 8 | Bonnet Gasket | EPDM / NBR | EPDM / NBR |
| 9 | Bonnet Nut | Brass | BS 2874-CZ 121 |
| 10 | Dust Seal | NBR | NBR |
| 11 | O-Rings (Stem Sealing) | NBR | NBR |
| 12 | O-Rings | NBR | NBR |
| 13 | Grooved Pin | Brass | BS 2874-CZ 121 |
| 14 | Handwheel Bolt | Stainless Steel | 304 |
| 15 | Thrust Collar | Brass | BS 2874-CZ 121 |

Dimensions (in mm)

OVERALL VALVES DIMENSIONS AND DRILLING DETAILS OF PN10 / PN16 FLANGES

| NOMINAL SIZE (DN) |  | OVERALL FACE TO FACE | OUTSIDE DIAMETER OF FLANGE |  | DIAMETER OF BOLT CIRCLE |  | HOLE NUMBER |  | DIAMETER OF BOLT HOLE |  | BOLT NOMINAL DIAMETER |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MM | INCHES |  | PN10 | PN16 | PN10 | PN16 | PN10 | PN16 | PN10 | PN16 | PN10 | PN16 |
| 80 | 3 | 229 | 200 | 200 | 160 | 160 | 8 | 8 | 19 | 19 | M16 | M16 |
| 100 | 4 | 254 | 220 | 220 | 180 | 180 | 8 | 8 | 19 | 19 | M16 | M16 |
| 150 | 6 | 280 | 285 | 285 | 240 | 240 | 8 | 8 | 23 | 23 | M20 | M20 |
| 200 | 8 | 317 | 340 | 340 | 295 | 295 | 8 | 12 | 23 | 23 | M20 | M20 |
| 25 | 10 | 356 | 395 | 405 | 350 | 355 | 12 | 12 | 23 | 28 | M20 | M24 |
| 300 | 12 | 380 | 445 | 460 | 400 | 410 | 12 | 12 | 23 | 28 | M20 | M24 |